ERV TEST & BALANCE REPORT

| PROJECT: | 63 Stockholm St |  | DATE: | 02/05/25 |
| --- | --- | --- | --- | --- |
| ADDRESS: | 63 Stockholm St, Brooklyn, NY |  | READINGS BY: | P.S. |
| PREPARED FOR: | All Cooling Inc |  | EQUIP. LOCATION: | Roof |

| UNIT DATA |  |  |  |  |  |  |  |  | EX MOTOR DATA |  |  |  | DESIGN |  | ACTUAL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UNIT # |  |  | ERV-3 |  |  |  |  |  | MANUFACTURER |  |  |  | - |  |  |  |
| UNIT TAG |  |  | ERV-3 |  |  |  |  |  | MODEL |  |  |  | - |  |  |  |
| LOCATION |  |  | Bulkhead |  |  |  |  |  | HP/BHP |  |  |  | .17/- |  | .17/- |  |
| AREA SERVED |  |  | Trash Rm/Corridor |  |  |  |  |  | PH/HZ/VOLT |  |  |  | 3/60/208 |  | 3/60/200 |  |
| UNIT TYPE |  |  | ERV |  |  |  |  |  | AMPS |  |  |  | 1.3 |  | - |  |
| MANUFACTURER |  |  | Ventacity Systems Inc |  |  |  |  |  | MOTOR RPM |  |  |  | 3653 |  | NVL |  |
| MODEL NUMBER |  |  | VS250 CMe (ERV) |  |  |  |  |  | FAN SET |  |  |  | 33% (35% offset) |  |  |  |
| SERIAL NUMBER |  |  | L24-23-ZOE2300028-3000268063 |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | OA MOTOR DATA |  |  |  | DESIGN |  | ACTUAL |  |
| PERFORMANCE DATA |  |  | DESIGN |  | ACTUAL |  |  |  | MANUFACTURER |  |  |  | - |  |  |  |
| EXHAUST AIR CFM |  |  | 95 |  | 99 |  |  |  | MODEL |  |  |  | - |  |  |  |
| OUTSIDE AIR CFM |  |  | 95 |  | 97 |  |  |  | HP/BHP |  |  |  | .17/- |  | .17/- |  |
|  |  |  |  |  |  |  |  |  | PH/HZ/VOLT |  |  |  | 3/60/208 |  | 3/60/200 |  |
| STATIC PROFILE |  |  | DESIGN |  | ACTUAL |  |  |  | AMPS |  |  |  | 1.3 |  | - |  |
| EXHAUST AIR SP |  |  | .50 |  | .95 |  |  |  | RPM |  |  |  | 3653 |  | NVL |  |
| OUTSIDE AIR sp |  |  | .50 |  | .96 |  |  |  | FAN SET |  |  |  | 68% (170 / 250 CFM) |  |  |  |
| UNIT AIR OUTLETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | EXHAUST AIR |  |  |  |  |  |  |  |  | OUTSIDE AIR |  |  |  |  |  |  |
| DWG # | # | DES CFM |  | VEL |  | ACT CFM |  | % |  | # | DES CFM | VEL |  | ACT CFM |  | % |
| M-104 | 1 | 10 |  | - |  | 10 |  | 100% |  | 1 | 15 |  |  | 16 |  | 107% |
| M-103 | 2 | 10 |  | - |  | 12 |  | 120% |  | 2 | 15 |  |  | 14 |  | 93% |
| M-102 | 3 | 10 |  | - |  | 9 |  | 90% |  | 3 | 15 |  |  | 14 |  | 93% |
| M-101 | 4 | 10 |  | - |  | 11 |  | 110% |  | 4 | 15 |  |  | 15 |  | 100% |
| M-100 | 5 | 55 |  | - |  | 57 |  | 104% |  | 5 | 25 |  |  | 27 |  | 108% |
|  |  |  |  |  |  |  |  |  |  | 6 | 10 |  |  | 11 |  | 110% |
| TOTAL |  | DES CFM |  | VEL |  | CFM |  | % |  | # | DES CFM | VEL |  | CFM |  | % |
|  |  | 95 |  | 0 |  | 99 |  | 104% |  |  | 95 | - |  | 97 |  | 102% |

| REMARKS: |  |
| --- | --- |