RTU TEST & BALANCE REPORT

| PROJECT: | Care365 Pomona |  | DATE: | 11/21/24 |
| --- | --- | --- | --- | --- |
| ADDRESS: | 1633 US-202, Pomona, NY |  | READINGS BY: | P.S. |
| PREPARED FOR: | Precision Mechanical |  | EQUIP. LOCATION: | Roof |

| UNIT DATA |  |  |  |  |  |  |  |  | MOTOR DATA |  |  |  |  | DESIGN |  | ACTUAL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UNIT TAG |  |  |  | RTU-1 |  |  |  |  | MANUFACTURER |  |  |  |  | GE Commercial Motors |  |  |  |
| LOCATION |  |  |  | Roof |  |  |  |  | MODEL |  |  |  |  | 5K48MN4671X |  |  |  |
| AREA SERVED |  |  |  | Exam Rooms |  |  |  |  | HP/BHP |  |  |  |  | 3/- |  | 3/- |  |
| UNIT TYPE |  |  |  | Package Roof Top |  |  |  |  | PH/HZ/VOLT |  |  |  |  | 1/60/208 |  | 1/60/208 |  |
| MANUFACTURER |  |  |  | American Slandered |  |  |  |  | AMPS |  |  |  |  | 5.5 |  | 3.1 |  |
| MODEL NUMBER |  |  |  | YSC072E3EHA0000 |  |  |  |  | MOTOR RPM |  |  |  |  | 1725 |  | 1738 |  |
| SERIAL NUMBER |  |  |  | 942101369L |  |  |  |  | FAN RPM |  |  |  |  | - |  | 916 |  |
|  |  |  |  |  |  |  |  |  | SF / EFF / PF |  |  |  |  | 1.5 / - / - / |  |  |  |
| PERFORMANCE DATA |  |  |  | DESIGN |  | ACTUAL |  |  | BELT NO. & SIZE |  |  |  |  | 1 / 34.2” (AX-32) |  |  |  |
| SUPPLY CFM |  |  |  | 1,350 |  | 1,216 |  |  | ADJ / FIXED |  |  |  |  | ADJ |  |  |  |
| RETURN CFM |  |  |  | - |  | - |  |  | MOTOR PITCH Ø SET |  |  |  |  | 1.5 Revolutions Open |  |  |  |
| OUTSIDE AIR CFM |  |  |  | N/A |  | N/A |  |  | MOTOR SHEAVE OD / BORE Ø |  |  |  |  | 3-3/4 / 5/8 |  |  |  |
|  |  |  |  |  |  |  |  |  | FAN SHEAVE OD / BORE Ø |  |  |  |  | 6” / 1” |  |  |  |
| CONTROLS |  |  |  |  |  |  |  |  | C TO C DISTANCE |  |  |  |  | - |  |  |  |
| MANUFACTURER |  |  |  | No Controls |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MODEL NUMBER |  |  |  | - |  |  |  |  | STATIC PROFILE |  |  |  |  | DESIGN |  | ACTUAL |  |
| SERIAL NUMBER |  |  |  | - |  |  |  |  | FILTER/COIL SP |  |  |  |  | - |  | .23 |  |
| CONTROL CONFIGURATION |  |  |  | - |  |  |  |  | RETURN SP |  |  |  |  | - |  | .27 |  |
| mAX AIRFLOW setpoint |  |  |  | - |  |  |  |  | SUPPLY SP |  |  |  |  | - |  | .29 |  |
| mIN AIRFLOW setpoint |  |  |  | - |  |  |  |  | TOTAL EXTERNAL SP |  |  |  |  | - |  | .56 |  |
|  |  |  |  |  |  |  |  |  | TOTAL SP |  |  |  |  | - |  | .80 |  |
| UNIT AIR OUTLETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | OUTLET |  |  |  |  |  | DESIGN CFM |  |  | PRELIMINARY |  |  | FINAL |  |  |  |  |
| DWG # | # | TYPE | SIZE |  | K-factor |  |  |  |  | VEL | CFM | % | VEL |  | CFM |  | % |
| M-100 | 1 | CD | 24x24 |  | .785 |  | 85 |  |  | - | - | - | - |  | 88 |  | 104% |
| M-100 | 2 | CD | 24x24 |  | .785 |  | 50 |  |  | - | - | - | - |  | 55 |  | 110% |
| M-100 | 3 | CD | 24x24 |  | .785 |  | 85 |  |  | - | - | - | - |  | 90 |  | 106% |
| M-100 | 4 | CD | 24x24 |  | .785 |  | 85 |  |  | - | - | - | - |  | 83 |  | 98% |
| M-100 | 5 | CD | 24x24 |  | .785 |  | 85 |  |  | - | - | - | - |  | 78 |  | 92% |
| M-100 | 6 | CD | 24x24 |  | .785 |  | 400 |  |  | - | - | - | - |  | 281 |  | 70% |
| M-100 | 7 | CD | 24x24 |  | .785 |  | 35 |  |  | - | - | - | - |  | 39 |  | 110% |
| M-100 | 8 | CD | 24x24 |  | .785 |  | 85 |  |  | - | - | - | - |  | 77 |  | 91% |
| M-100 | 9 | CD | 24x24 |  | .785 |  | 35 |  |  | - | - | - | - |  | 38 |  | 109% |
| M-100 | 10 | CD | 24x24 |  | .785 |  | 35 |  |  | - | - | - | - |  | 36 |  | 103% |

| REMARKS: |  |
| --- | --- |