RTU TEST & BALANCE REPORT

| PROJECT: | Belmont Apartments |  | DATE: | 07/08/24 |
| --- | --- | --- | --- | --- |
| ADDRESS: | 27 3rd Avenue Long Branch NJ |  | READINGS BY: | P.S. |
| PREPARED FOR: | EnerCode Solutions |  | EQUIP. LOCATION: | Roof |

| UNIT DATA |  |  |  |  |  |  |  |  | MOTOR DATA |  |  |  | DESIGN |  |  | ACTUAL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UNIT # |  |  |  | RTU-1 |  |  |  |  | MANUFACTURER |  |  |  | PROTECH MOTORS |  |  |  |  |
| UNIT TAG |  |  |  | RTU-1 |  |  |  |  | MODEL |  |  |  | 5SME39NX |  |  |  |  |
| LOCATION |  |  |  | Roof |  |  |  |  | HP/BHP |  |  |  | .75/- |  |  | .75/- |  |
| AREA SERVED |  |  |  | Corridor Floors 2-4 |  |  |  |  | PH/HZ/VOLT |  |  |  | 1/60/208 |  |  | 1/60/210 |  |
| UNIT TYPE |  |  |  | RTU |  |  |  |  | AMPS |  |  |  | 6.0 |  |  | 3.3 |  |
| MANUFACTURER |  |  |  | Rheem |  |  |  |  | MOTOR RPM |  |  |  | 1050 |  |  | - |  |
| MODEL NUMBER |  |  |  | RGECZR036ACT102AC |  |  |  |  | SF / EFF / PF |  |  |  | - |  |  |  |  |
| SERIAL NUMBER |  |  |  | F032301887 |  |  |  |  | FAN SPEED SET |  |  |  | Second Stage Fan |  |  |  |  |
| PERFORMANCE DATA |  |  |  | DESIGN |  | ACTUAL |  |  | CONTROLS |  |  |  |  |  |  |  |  |
| SUPPLY CFM |  |  |  | 1200 |  | 1219 |  |  | MANUFACTURER |  |  |  | Honeywell |  |  |  |  |
| RETURN CFM |  |  |  | - |  | - |  |  | MODEL NUMBER |  |  |  | W7220A |  |  |  |  |
| OUTSIDE AIR CFM |  |  |  | 240 |  | 217 |  |  | SERIAL NUMBER |  |  |  | A10002240J6561 |  |  |  |  |
|  |  |  |  |  |  |  |  |  | oa minimum position |  |  |  | 2.65 v |  |  |  |  |
| STATIC PROFILE |  |  |  | DESIGN |  | ACTUAL |  |  | Economize setpoint |  |  |  | 70°F (ES3) |  |  |  |  |
| FILTER/COIL SP |  |  |  | - |  | 0.11 / 0.10 |  |  |  |  |  |  |  |  |  |  |  |
| RETURN SP |  |  |  | - |  | 0.47 |  |  |  |  |  |  |  |  |  |  |  |
| SUPPLY SP |  |  |  | - |  | 0.62 |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL EXTERNAL SP |  |  |  | .75 |  | 1.1 |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL SP |  |  |  | - |  | 1.3 |  |  |  |  |  |  |  |  |  |  |  |
| UNIT AIR OUTLETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | OUTLET |  |  |  |  |  | DESIGN CFM |  |  | PRELIMINARY |  |  |  | FINAL |  |  |  |
| DWG # | # | TYPE | SIZE |  | K-factor |  |  |  |  | VEL | CFM | % |  | VEL | CFM |  | % |
| M-204 | 1 | CD | 10x10 |  | 1.48 |  | 200 |  |  | - | - | - |  | - | 187 |  | 94% |
| M-204 | 2 | CD | 10x10 |  | 1.48 |  | 200 |  |  | - | - | - |  | - | 181 |  | 91% |
| M-203 | 3 | CD | 10x10 |  | 1.48 |  | 200 |  |  | - | - | - |  | - | 219 |  | 110% |
| M-203 | 4 | CD | 10x10 |  | 1.48 |  | 200 |  |  | - | - | - |  | - | 221 |  | 111% |
| M-202 | 5 | CD | 10x10 |  | 1.48 |  | 200 |  |  | - | - | - |  | - | 192 |  | 96% |
| M-202 | 6 | CD | 10x10 |  | 1.48 |  | 200 |  |  | - | - | - |  | - | 219 |  | 110% |
| TOTAL |  |  |  |  |  |  | CFM |  |  | VEL | CFM | % |  | VEL | CFM |  | % |
|  |  |  |  |  |  |  | 1200 |  |  | - | - | - |  | - | 1219 |  | 102% |

| REMARKS: |  |
| --- | --- |