FAN TEST & BALANCE REPORT

| PROJECT: | Alexander Yeshiva |  | DATE: | 04/24/25 |
| --- | --- | --- | --- | --- |
| ADDRESS: | 1637 62nd St, Brooklyn, NY |  | READINGS BY: | P.S. |
| PREPARED FOR: | Cityscape Builders LLC |  | EQUIP. LOCATION: | Paper Goods Storage |

| UNIT DATA |  |  |  |  |  |  |  |  |  | MOTOR DATA |  |  |  | DESIGN |  |  | ACTUAL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UNIT TAG |  |  |  | EF-1-1 |  |  |  |  |  | MANUFACTURER |  |  |  | - |  |  |  |  |
| LOCATION |  |  |  | Roof |  |  |  |  |  | MODEL |  |  |  | - |  |  |  |  |
| AREA SERVED |  |  |  | Paper Goods Storage |  |  |  |  |  | HP/BHP |  |  |  | - |  |  | - |  |
| UNIT TYPE |  |  |  | Inline Fan |  |  |  |  |  | PH/HZ/VOLT |  |  |  | 1/60/120 |  |  | 1/60/- |  |
| MANUFACTURER |  |  |  | Fantech |  |  |  |  |  | AMPS |  |  |  | .29 |  |  | NVL |  |
| MODEL NUMBER |  |  |  | PrioAir 6 |  |  |  |  |  | MOTOR RPM |  |  |  | - |  |  | - |  |
| SERIAL NUMBER |  |  |  | 1007804622 |  |  |  |  |  | SF / EFF / PF |  |  |  | - |  |  |  |  |
| PERFORMANCE DATA |  |  |  | DESIGN |  | ACTUAL |  |  |  | CONTROLS |  |  |  |  |  |  |  |  |
| TOTAL CFM |  |  |  | 145 |  | 105 |  |  |  | MANUFACTURER |  |  |  | No Controls |  |  |  |  |
| SUCTION SP |  |  |  |  |  |  |  |  |  | MODEL |  |  |  |  |  |  |  |  |
| DISCHARGE SP |  |  |  |  |  |  |  |  |  | CONFIGURATION |  |  |  |  |  |  |  |  |
| TOTAL SP |  |  |  |  |  |  |  |  |  | SETPOINT |  |  |  |  |  |  |  |  |
| UNIT AIR OUTLETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | OUTLET |  |  |  |  |  |  | DESIGN CFM |  |  | PRELIMINARY |  |  |  | FINAL |  |  |  |
| DWG # | # | TYPE | SIZE |  | K-factor |  |  |  |  |  | FPM | CFM | % |  | FPM | CFM |  | % |
| M-100 | 10 | CG | 6x6 |  | 1.0 (TSI) |  |  | 70 |  |  | - | - | - |  | - | 57 |  | 81% |
| M-100 | 11 | CG | 6x6 |  | 1.0 (TSI) |  |  | 75 |  |  | - | - | - |  | - | 48 |  | 64% |
| TOTAL |  |  |  |  |  |  |  | CFM |  |  | VEL | CFM | % |  | VEL | CFM |  | % |
|  |  |  |  |  |  |  |  | 145 |  |  | - | - | - |  | - | 105 |  | 72% |

| REMARKS: |  |
| --- | --- |