RTU TEST & BALANCE REPORT

| PROJECT: | Alexander Yeshiva |  | DATE: | 04/07/25 |
| --- | --- | --- | --- | --- |
| ADDRESS: | 1637 62nd St, Brooklyn, NY |  | READINGS BY: | P.S. |
| PREPARED FOR: | Cityscape Builders LLC |  | EQUIP. LOCATION: | Roof |

| UNIT DATA |  |  |  |  |  |  |  |  | MOTOR DATA |  |  |  |  | DESIGN |  | ACTUAL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UNIT TAG |  |  |  | RTU-1 |  |  |  |  | MANUFACTURER |  |  |  |  | Baldor Reliance |  |  |  |
| LOCATION |  |  |  | Roof |  |  |  |  | MODEL |  |  |  |  | 1151209 |  |  |  |
| AREA SERVED |  |  |  | YG Shul |  |  |  |  | HP/BHP |  |  |  |  | 3.7 / - |  | 3 / - |  |
| UNIT TYPE |  |  |  | Package Roof Top |  |  |  |  | PH/HZ/VOLT |  |  |  |  | 1/60/208 |  | 1/60/207 |  |
| MANUFACTURER |  |  |  | Johnson Controls |  |  |  |  | AMPS |  |  |  |  | 9.6 |  | 6.7 |  |
| MODEL NUMBER |  |  |  | AD15S3CQ2J1A8T47E2 |  |  |  |  | MOTOR RPM |  |  |  |  | 1750 |  | 1409 |  |
| SERIAL NUMBER |  |  |  | N2B4145800 |  |  |  |  | FAN RPM |  |  |  |  | - |  | 671 |  |
|  |  |  |  |  |  |  |  |  | SF / EFF / PF |  |  |  |  | 1.5 / .87 / 81 |  |  |  |
| PERFORMANCE DATA |  |  |  | DESIGN |  | ACTUAL |  |  | BELT NO. & SIZE |  |  |  |  | 1 / 43” (AX-41) |  |  |  |
| SUPPLY CFM |  |  |  | 4,125 |  | 4,547 |  |  | MOTOR PITCH Ø SET |  |  |  |  | 3 Revolutions Open |  |  |  |
| RETURN CFM |  |  |  | - |  | - |  |  | MOTOR SHEAVE OD / BORE Ø |  |  |  |  | - |  |  |  |
| OUTSIDE AIR CFM |  |  |  | 900 |  | 916 |  |  | FAN SHEAVE OD / BORE Ø |  |  |  |  | 7.68” / .50” (1B5V74) |  |  |  |
|  |  |  |  |  |  |  |  |  | C TO C DISTANCE |  |  |  |  | - |  |  |  |
| CONTROLS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FAN ONLY |  |  |  | *68% |  |  |  |  | STATIC PRESSURE PROFILE |  |  |  |  | DESIGN |  | ACTUAL |  |
| FAN HEATING |  |  |  | 79% |  |  |  |  | RETURN SP |  |  |  |  | - |  | .14 |  |
| fan COOLING STAGE 1/2/3/4 |  |  |  | 68% / 71% / 79% / 79% |  |  |  |  | FILTER SP |  |  |  |  |  |  | .04 |  |
| ECONOMIZER MIN POSITION |  |  |  | Marked on Unit |  |  |  |  | COIL SP |  |  |  |  |  |  | .09 |  |
| MIN POSITION LOW SPEED |  |  |  | No Controls |  |  |  |  | SUPPLY SP |  |  |  |  | - |  | .46 |  |
| ECONOMIZE ENABLE BASED ON |  |  |  | No Controls |  |  |  |  | TOTAL EXTERNAL SP |  |  |  |  | 1.0 |  | .64 |  |
| ECONOMIZE SET Temp / Δh |  |  |  | No Controls |  |  |  |  | TOTAL SP |  |  |  |  | - |  | .73 |  |
| UNIT AIR OUTLETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | OUTLET |  |  |  |  |  | DESIGN CFM |  |  | PRELIMINARY |  |  | FINAL |  |  |  |  |
| DWG # | # | TYPE | SIZE |  | K-factor |  |  |  |  | VEL | CFM | % | VEL |  | CFM |  | % |
| M-102 | 1 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 442 |  | 118% |
| M-102 | 2 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 449 |  | 120% |
| M-102 | 3 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 593 |  | 158% |
| M-102 | 4 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 501 |  | 134% |
| M-102 | 5 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 307 |  | 82% |
| M-102 | 6 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 648 |  | 173% |
| M-102 | 7 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 328 |  | 87% |
| M-102 | 8 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 355 |  | 95% |
| M-102 | 9 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 259 |  | 69% |
| M-102 | 10 | CD | 24x24 |  | .91 |  | 375 |  |  | - | - | - | - |  | 260 |  | 69% |

| REMARKS: | *Fan-only speed set, to maintain Minimum Outside Air. |
| --- | --- |