FCU TEST & BALANCE REPORT

| PROJECT: | ODA Primary Health Care |  | DATE: |  |
| --- | --- | --- | --- | --- |
| ADDRESS: | 251 Wallabout St, Brooklyn, NY |  | READINGS BY: | P.S. |
| PREPARED FOR: | Active Cooling |  | EQUIP. LOCATION: |  |

| UNIT DATA |  |  |  |  |  |  |  |  | MOTOR DATA |  |  |  | DESIGN |  |  | ACTUAL |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| UNIT # |  |  |  |  |  |  |  |  | MANUFACTURER |  |  |  | WOLONG |  |  |  |  |
| UNIT TAG |  |  |  |  |  |  |  |  | MODEL NUMBER |  |  |  | - |  |  |  |  |
| AREA SERVED |  |  |  |  |  |  |  |  | HP/BHP |  |  |  | / - |  |  | / - |  |
| UNIT TYPE |  |  |  |  |  |  |  |  | PH/HZ/VOLT |  |  |  | 1/60/208 |  |  | 1/60/207 |  |
| MANUFACTURER |  |  |  |  |  |  |  |  | AMPS |  |  |  |  |  |  |  |  |
| MODEL NUMBER |  |  |  |  |  |  |  |  | MOTOR RPM |  |  |  | - |  |  | - |  |
| SERIAL NUMBER |  |  |  |  |  |  |  |  | FAN SPEED SET |  |  |  |  |  |  |  |  |
| PERFORMANCE DATA |  |  |  | DESIGN |  | ACTUAL |  |  | STATIC PRESSURE |  |  |  | DESIGN |  |  | ACTUAL |  |
| TOTAL SUPPLY CFM |  |  |  |  |  |  |  |  | RETURN SP |  |  |  | - |  |  |  |  |
| TOTAL RETURN CFM |  |  |  |  |  |  |  |  | SUPPLY SP |  |  |  | - |  |  |  |  |
| TOTAL OA CFM |  |  |  |  |  |  |  |  | TOTAL EXTERNAL SP |  |  |  |  |  |  |  |  |
| UNIT AIR OUTLETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | OUTLET |  |  |  |  |  | DESIGN CFM |  |  | PRELIMINARY |  |  |  | FINAL |  |  |  |
| DWG # | # | TYPE | SIZE |  | K-factor |  |  |  |  | VEL | CFM | % |  | VEL | CFM |  | % |
| M-101 | 1 | CD | 12x12 |  | 1.02 |  | 150 |  |  | - | - | - |  | 400 | 145 |  | 97% |
|  |  | LSD | 24x6 |  | 1.02 |  |  |  |  | - | - | - |  | - |  |  |  |
|  |  | LSD | 24x6 |  | 1.02 |  |  |  |  | - | - | - |  | - |  |  |  |
|  |  | LSD | 24x6 |  | 1.02 |  |  |  |  | - | - | - |  | - |  |  |  |
|  |  | LSD | 24x6 |  | 1.02 |  |  |  |  | - | - | - |  | - |  |  |  |
|  |  | LSD | 24x6 |  | 1.02 |  |  |  |  |  |  |  |  |  |  |  |  |
| TOTAL |  |  |  |  |  |  | CFM |  |  | VEL | CFM | % |  | VEL | CFM |  | % |
|  |  |  |  |  |  |  |  |  |  | - | - | - |  | - |  |  |  |
| M-101 | 2 | CD | 12x12 |  | 1.02 |  | 120 |  |  | - | - | - |  | 380 | 118 |  | 98% |

| REMARKS: |  |
| --- | --- |